## Ice Arena Entry
ICE ARENA DEHUMIDIFICATION LOAD
Version 1.0 - 2026
PROJECT |  | Raising Canes' Arena
LOCATION |  | Baton Rouge, LA
TOTAL MOISTURE LOAD |  | 1098.8449 |  | lb/hr
QUICK ENTRY GUIDE
Blue = editable input ¦ Gray = calculated value ¦ Green = final total ¦ Inputs: rows 19–39 ¦ Loads: rows 45–90
Design Parameters |  |  |  | Guidance
Outside Air Conditions
Baton Rouge, LA | Location | 82 | °F DB
Raising Canes' Arena | Project Name | 129.7 | gr/lb
|  | 6.9 | Wind Speed (mph)
|  | 607.2 | Wind Speed (FPM)
Rink Conditions / Size
60 | °F DB | 270 | L (ft)
30.7 | gr/lb | 146 | W (ft)
35.6 | °F Dew Point | 37 | H (ft)
Ice Surface
16327 | Area (sqft) |  |  | NHL: 16327 sqft, Olympic: 19327 sqft
People
250 | # Spectators
20 | # Skaters
Moisture Load Sources |  |  |  | Guidance
Infiltration
1458540 | Building Volume (ft3)
0.4 | ACH |  |  | 0.2 - 1 ACH (Excellent - Poor construction)
9723.6 | CFM | 618.8377 | lb/hr
Ventilation Air
39420 | Building Area (ft2)
People O/A Rate (Rp)
7.5 | Spectators (CFM/Person) |  |  | Ashrae 62.1, 2022
20 | Skaters (CFM/Person) |  |  | Ashrae 62.1, 2022
2275 | CFM
Space O/A Rate (Ra)
0.06 | Building (CFM/ft2) |  |  | Ashrae 62.1, 2022
0.18 | Rink (CFM/ft2) |  |  | Ashrae 62.1, 2022
4324.44 | CFM
Breathing Zone O/A Rate (Vbz)
6599.44 | Total OA (CFM) |  |  | Vbz = (Rp*Pz)+(Ra*Az)
|  | 420.0072 | lb/hr | Outside ventilation/make-up Air
Spectators
0.1 | lb/hr | 25 | lb/hr | 0.1 - 1 lb/hr (Seated - Very Active)
Skaters
0.5 | lb/hr | 10 | lb/hr | 0.1 - 1 lb/hr (Seated - Very Active)
Exterior Doors
0 | # Qty |  |  | Exterior door load uses average wind speed
3 | W (ft)
7 | H (ft)
1 | Open Time (min/hr) | 0 | lb/hr
Ice Resurfacing
25 | lb/hr | 25 | lb/hr | Estimation of water evaporation during resurfacing
| Total | 1098.8449 | lb/hr